REQUEST FOR QUOTATION AND DELIVERY SCHEDULES

FOR PURCHASE OF

FIBER OPTICS INNERDUCT AND CABLE

for

THE UNIVERSITY OF CALIFORNIA AT SANTA BARBARA

June, 1995

Department of Communications Services

University of California

at

Santa Barbara

# SECTION 1  PURCHASING LETTER

## 1.1     Purpose

The purpose of this Request For Quotation (RFQ) is to provide the University of California, Santa Barbara campus (UCSB), with the specifications, delivery information and price quotations for purchase of fiber optic innerduct and fiber optic cable. The RFQ includes Bid Alternative One for purchase of composite fiber cable.

## 1.2     Issuing Office

This RFQ  is issued  for the University by  the  Purchasing Department. Quotations must  be received  by 4:30 p.m. on July 14, 1995 and submitted in three (3) copies to:

Oscar Woolfolk

Purchasing Department

University of California

Santa Barbara, CA 93106

(805) 893-3086  (fax)  (805) 893-8639

Technical Contact:	David Chapman  (805) 893-4030

## 1.3    Terms and Conditions

The terms and conditions specified in Appendix A shall apply.

## 1.4     Definitions

For the sake of brevity, the following definitions should be used whenever the following  terms are used throughout the RFQ:

Composite Cable:

The forty-eight (48) multi-mode and twelve (12) single mode fiber optical cable defined in this document which may be acquired as a result of this RFQ. (Bid Alternative One)

Multi-mode Cable:

The forty-eight (48) multi-mode fiber optical cable defined in this document which may be acquired as a result of this RFQ.

Innerduct:

The rigid, non-metallic protective sheath installed within a duct system to house the present and future fiber cable.

Segment:

A continuous section of fiber optic cable or innerduct delivered on a cable reel. Multiple segments may be delivered on a single reel according to ordering instructions.

UCSB:

Refers to the University of California, Santa Barbara campus, only.

University:

Refers to the University of California, Santa Barbara campus, only.

The Vendor:

The individual, partnership or corporation, who, as a result of the bidding process, is selected to provide the fiber optic innerduct and fiber optic cable.

## 1.5    Quotation Reference Number

All quotations shall reference the RFQ number - OW 4746-ED.

## 1.6    Addenda

No one is authorized  to amend any part of this Request For Quotation, in any respect,  by oral statement, or to make representation or interpretation in conflict with its provisions. The University may modify this Request For Quotation, prior to the date of its acceptance, by issuance of written addenda to all parties who have received the original RFQ. The date fixed for submission of quotations may be extended, if in the sole judgment of  the University, it is warranted.  All addenda will clearly be marked as such.  Failure of any qualified bidder to receive such addenda or interpretation shall not relieve such bidder from any obligation under their bid as  submitted. All addenda so issued shall become part of  the Request  For Quotation documents.

## 1.7    Contract Award in Best Interest

The University reserves the right to accept  or  reject quotations on each item separately or as a whole, to reject any or all quotations without penalty, to waive informalities or irregularities, and to contract as the best interest of the University may require in order  to obtain the materials which best meets the needs of the University as expressed in this RFQ.

## 1.8    Right to Reject or Modify

Selection of  the winning Vendor's quotation does not mean that all aspects of the quotation(s) are acceptable to the University. The University retains the right to modify the terms and conditions in the quotation(s) or reject terms and conditions proposed by the Vendor prior to the execution of the contract as the University, at its sole discretion,

deems necessary to ensure a satisfactory procurement.

## 1.9    Vendors Quotations

To facilitate consideration of their quotations, Vendors must submit three (3) complete copies of all bid documents, in the format described.

## 1.10    Warranty

All materials provided by the selected Vendor shall have a minimum on-site warranty period of one (1) year from the date specified in the written Notice of Final Acceptance.

## 1.11    Defect Notification

The Vendor shall receive detailed notification of all defective or unacceptable material  from the University, which shall be replaced to the satisfaction of the University's

representative. The replacement shall be made by the Vendor within thirty (30)  days after notification by the University.

## 1.12    Selection Criteria

Quotations will be evaluated by a University Evaluation Team. The contract award, if made, will be made to the Vendor who has the ability to do the following:

### 1.12.1 Meet all material specifications and requirements of this RFQ,

### 1.12.2 Meet or exceed the stated schedule for provision of all materials,

### 1.12.3 Award(s) shall be made to the lowest responsible bidder meeting specifications, or else all quotations shall be rejected. Using this method, all items other than price are specifications that must be met in order for the quotation to be considered.

## 1.13    Contract Changes

After selection of the successful bidder, UCSB may contract for any changes in the total footage of fiber innerduct and/or cable. UCSB may contract for the fiber optic innerduct and either the multi-mode fiber cable or the composite multi-mode and single-mode cable (Bid Alternative One), but not both.

## 1.14    Price Quotation

All quotations for the purchase prices of products stated in the Vendor's quotation should be fixed from the date on which the quotation is submitted by the Vendor for a period of one hundred and eighty (180) days to allow the University to make two (2) separate acquisitions of fiber optic cable and innerduct. If the Vendor is not able to fix the price for one hundred and eighty (180) days, please indicate how many days the Vendor will fix the price.

Price fixed for  _____________   days.

## 1.15    Fiber Performance Test Requirements

### The University will subject the fiber optic cable received to testing:

### 1.15.1  The delivered cable must contain a complete record of factory testing. The factory testing must include a signal loss measurement (in db) at 1300nm for each multi-mode fiber in the cable. This measurement must be made for each fiber within each cable segment on each reel.

### 1.15.2  The factory testing must include a signal loss measurement (in db) at 1310nm for each single mode fiber in the cable. This measurement must be made for each fiber within each fiber optic cable segment on each reel (Bid Alternative One).

### 1.15.3  On-site testing of the fiber optic cable, on the reel(s) will take place within three (3) working days of receipt of the complete shipment of cable, including all documentation. Vendor will be notified of acceptance or rejection of cable within five (5) working days of completion of testing.

### 1.15.4  The on-site testing of the fiber optic cable, on the reel(s), must produce measurements within 3% of the original factory measurements or the design specifications of the cable. If any part of the measurement, on any reel, produces results which are outside of these specifications, the entire reel will be rejected and subjected to re-measurement by the vendor and replacement, at no additional cost to the University.

## 1.16 	Schedule for RFQ Quotation and Delivery

The schedule for this RFQ is as follows:

### June 23, 1995: RFQ issued by University Purchasing Department.

### July 7-14, 1995: Vendor's response to the RFQ due in Purchasing Department.

### July 21, 1995: Complete evaluation of RFQ responses and select successful bidder.

### July 28, 1995:  Deadline for delivery of innerduct to the campus.

### August 29, 1995:  Deadline for delivery of fiber optic cable to the campus.

### The University may extend these dates, at its sole discretion.

# SECTION 2    BACKGROUND FOR THE QUOTATION

## 2.1	OBJECTIVE

The objective of this Request for Quotation (RFQ) is to solicit material specifications, cost quotations, and delivery schedules for the acquisition of fiber optic innerduct and fiber optic cable for the campus. The campus is preparing to construct two additional fiber optic cable rings.

Ring three has been funded and will require seventeen-thousand, five hundred feet (17,500') of fiber optic cable and approximately seventy-seven hundred feet (7,700') of both one inch and one and one-quarter inch innerduct. This amount of fiber optic cable and innerduct, in either multi-mode or composite (see 2.2 Alternative) will be immediately purchased as a result of this bid.

Campus fiber optic cable ring four has not yet been funded and purchase of the fiber optic cable and innerduct required for this ring may be delayed up to one hundred and eighty (180) days.

## 2.2	ALTERNATIVE

Subject to cost quotations supplied by Vendors as a result of this RFQ, the University may choose to acquire a composite (multi-mode and single mode in a single sheath) fiber optic cable (Bid Alternative One) in lieu of multi-mode only cable.

# SECTION 3    TECHNICAL SPECIFICATIONS AND REQUIREMENTS

The specifications in this section represent the minimum capabilities required of the components and levels of service required of the Vendor. Prospective Vendors must provide full responses to these requirements, in the format specified in Section 4 (Vendor Submittals) of this RFQ.

## 3.1 	Multi-Mode Fiber Cable Specification

### 3.1.1  Number of  Operational Fibers

#### 3.1.1.1 The minimum number of available multi-mode fibers shall be at least forty-eight (48) in a common sheath cable.

#### 3.1.1.2 There shall be a minimum of forty-eight (48) operational multi-mode fibers meeting all specifications in each cable segment shipped.

#### 3.1.1.3 Fibers in excess of the specified operational fibers shall be labeled as such and stored as spares for warranty repairs upon completion of University installation and testing.

### 3.1.2.  Fiber Optic Cable Construction

#### 3.1.2.1  All fiber optic cable shall be equivalent to Siecor specification number 048K14-14110-20.

#### 3.1.2.2  The 48 fiber optic cable sheath shall have an outside diameter equal to or less than fifteen (15) millimeters (mm).

#### 3.1.2.3  No fluid or gas filled cable is permitted.

#### 3.1.2.4  The fiber optic cable shall be non-armored and have no metallic components.

#### 3.1.2.5  The central strength member shall be of all-dielectric construction.

#### 3.1.2.6  The forty-eight (48) fibers shall be grouped within the cable sheath into four (4) buffer tubes of twelve (12) fibers per buffer tube.

#### 3.1.2.7  Buffer tube shall be of  "loose tube" construction.

#### 3.1.2.8  Fiber buffer tube groups shall be uniquely identified.

#### 3.1.2.9  The optical fibers shall be constructed of all glass with a multi-mode graded index profile.

#### 3.1.2.10  Exclusive of protective buffer jacket coatings, each multi-mode fiber shall have an outer diameter of 125.0 +/- 2.0 microns and a core diameter of 62.5 +/- 3.0 microns.

#### 3.1.2.11  Fibers shall be individually color coded within each sub-grouping in the cable.

#### 3.1.2.12  The numerical aperture for each optical multi-mode fiber in all cables shall be 0.275 +/- 0.02.

#### 3.1.2.13  The attenuation value of each optical multi-mode fiber shall not exceed 1.00 db/km measured at 1300 nm over the temperature range of 0 to 150 degrees Fahrenheit.

#### 3.1.2.14  The measured bandwidth of each optical multi-mode fiber shall be a minimum of 500 MHz at 1300 nm.

#### 3.1.2.15  The measured bandwidth of each optical multi-mode fiber shall be a minimum of 160 MHz at 850 nm.

#### 3.1.2.16  Inclusions manifested as attenuation spikes in an optical fiber shall not exceed 0.2 db or 50% of the total attenuation in that fiber, whichever is less.

#### 3.1.2.17  Only one inclusion perturbation will be allowed per fiber in each cable segment.

#### 3.1.2.18  The fiber optic cable shall be capable of withstanding temperatures of 0 to 150 degrees Fahrenheit for an indefinite period of time without physical damage or alteration of its operating characteristics.

### 3.1.3  Manufacturer's Label

#### The outer jacket of the fiber optic cable shall have a permanent label in a highly visible color at a regular interval of not more than ten feet (10') containing at least the following:

#### 3.1.3.1  The manufacturer of the cable.

#### 3.1.3.2  A legend similar to "FIBER OPTIC CABLE".

#### 3.1.3.3  A footage or meter marker.

#### 3.1.3.4  The number of fibers within the cable.

## 3.2	Composite Fiber Cable Specification  (Bid Alternative One)

### 3.2.1  Composite Cable - Number of  Operational Fibers (Bid Alternative One)

#### 3.2.1.1 The minimum number of available multi-mode fibers shall be forty-eight (48) and the minimum number of available single-mode fibers shall be twelve (12) in a common sheath cable.

#### 3.2.1.2 There shall be a minimum of forty-eight (48) operational multi-mode fibers and a minimum of twelve (12) operational single mode fibers meeting all specifications in the common sheath cable.

#### 3.2.1.3  Fibers provided by the Vendor in excess of the specified operational fibers shall be labeled as such and reserved as spares for warranty repairs upon completion of University installation and testing.

### 3.2.2  Composite Fiber Optic Cable  - Construction (Bid Alternative One)

#### 3.2.2.1.  Cable construction shall be equivalent to Siecor specification number series 060X14-141XX-20 for hybrid mini bundle cable.

#### 3.2.2.2.  The 60 fiber [forty-eight (48) multi-mode and twelve (12) single mode] fiber optic cable sheath shall have an outside diameter equal to or less than fifteen (15) millimeters (mm).

#### 3.2.2.3.  No fluid or gas filled cable is permitted.

#### 3.2.2.4.  The fiber optic cable shall be non-armored and have no metallic components.

#### 3.2.2.5.  The central strength member shall be of all-dielectric construction.

#### 3.2.2.6. The forty-eight (48) multi-mode fibers shall be grouped within the cable sheath into four (4) buffer tubes of twelve (12) fibers per buffer tube.

#### 3.2.2.7  The twelve (12) single-mode fibers shall be grouped within the cable sheath into a single (1) buffer tube of twelve (12) fibers.

#### 3.2.2.8.  Buffer tube shall be of  "loose tube" construction.

#### 3.2.2.9.  Fiber buffer tube groups shall be uniquely identified.

### 3.2.3  Composite Fiber Optic Cable - Multi-mode Fiber Component

#### (Bid Alternative One)

#### 3.2.3.1.  The optical fibers shall be constructed of all glass with a graded index profile.

#### 3.2.3.2.  Each multi-mode fiber shall have a core diameter of 62.5 +/- 3.0 microns.

#### 3.2.3.3.  Each multi-mode fiber shall have a cladding diameter of 125 +/- 2 microns and a coating diameter of 250 +/1 15 microns

#### 3.2.3.4.  Fibers shall be individually color coded within each sub-grouping in the cable.

#### 3.2.3.5.  The numerical aperture for each optical multi-mode fiber in all cables shall be 0.275 +/- 0.015.

#### 3.2.3.6.  The attenuation value of each optical multi-mode fiber shall not exceed 1.00 db/km measured at 1300 nm over the temperature range of 0 to 150 degrees Fahrenheit.

#### 3.2.3.7.   The measured bandwidth of each optical multi-mode fiber shall be a minimum of 500 MHz at 1300 nm.

#### 3.2.3.8.  The measured bandwidth of each optical multi-mode fiber shall be a minimum of 160 MHz at 850 nm.

#### 3.2.3.9.  Inclusions manifested as attenuation spikes in an optical multi-mode fiber shall not exceed 0.2 db or 50% of the total attenuation in that fiber, whichever is less.

#### 3.2.3.10.  Only one inclusion perturbation will be allowed per fiber per segment.

#### 3.2.3.11.  The fiber optic cable shall be capable of withstanding temperatures of 0 to 150 degrees Fahrenheit for an indefinite period of time without physical damage or alteration of its operating characteristics.

### 3.2.4  Composite Fiber Optic Cable - Single Mode Fiber Component

#### (Bid Alternative One)

#### 3.2.4.1   The optical fibers shall be constructed of all glass with a single grade index profile.

#### 3.2.4.2   Each single mode fiber shall have a core diameter of 9.3 +/- 0.50 microns.

#### 3.2.4.3  Each single mode fiber shall have a cladding diameter of 125 +/- 1.0 micron and a coating diameter of  250 +/- 15 microns.

#### 3.2.4.4   Fibers shall be individually color coded within each sub-grouping in the cable.

#### 3.2.4.5   Dispersion in each single mode fiber will be less than or equal to 2.8 psec/nm/km at 1310nm +/- 20 microns.

#### 3.2.4.6   Dispersion in each single mode fiber will be less than or equal to 18 psec/nm/km at 1550nm +/- 20 microns.

#### 3.2.4.7   The attenuation value of each single mode fiber shall not exceed 0.4 db/km measured at 1310 nm over the temperature range of 0 to 150 degrees Fahrenheit.

#### 3.2.4.8   The attenuation value of each single mode fiber shall not exceed 0.3 db/km measured at 1550 nm over the temperature range of 0 to 150 degrees Fahrenheit.

#### 3.2.4.9   The measured bandwidth of each single mode fiber shall be a minimum of 500 MHz at 1310 nm and 1550 nm.

#### 3.2.4.10   Inclusions manifested as attenuation spikes in a single mode optical fiber shall not exceed 0.2 db or 50% of the total attenuation in that fiber, whichever is less.

#### 3.2.4.11  Only one inclusion perturbation will be allowed per fiber per cable segment.

#### 3.2.4.12   The fiber optic cable shall be capable of withstanding temperatures of 0 to 150 degrees Fahrenheit for an indefinite period of time without physical damage or alteration of its operating characteristics.

### 3.2.5  Composite Fiber Optic Cable - Manufacturer's Label

#### (Bid Alternative One)

### The outer jacket of the fiber optic cable shall have permanent identification in a highly visible color at a regular interval of not more than ten feet (10') containing at least the following:

#### 3.2.5.1  The manufacturer of the cable.

#### 3.2.5.2  A legend similar to "FIBER OPTIC CABLE".

#### 3.2.5.3  A footage or meter marker.

#### 3.2.5.4  The fiber count within the cable, including reference to both multi-mode and single mode fiber counts.

## 3.3   Fiber Optic Innerduct

### 3.3.1  Innerduct - One and one-quarter inch (1.25") Diameter

#### 3.3.1.1  Innerduct shall be equivalent to Duraline specification PE3408 for ribbed innerduct.

#### 3.3.1.2  Construction shall be of high density polyethylene

#### 3.3.1.3  Innerduct shall be supplied by the manufacturer with a measured pull line in increments not greater than one meter.

#### 3.3.1.4  Pull strength of innerduct shall be a minimum of sixteen hundred (1600) pounds.

#### 3.3.1.5  Tensil strength at breaking shall be not less than 4000 psi (ASTM

#### D-638 test method).

#### 3.3.1.6   In-duct pull line shall have a breaking strength of not less than twelve hundred (1200) pounds.

#### 3.3.1.7  Minimum bend radius shall be twelve inches (12").

#### 3.3.1.8  Inside diameter shall be 1.250" +/- 0.015".

#### 3.3.1.8  Outside diameter shall be 1.580" +/- 0.020".

### 3.3.2  Innerduct - One inch (1.00") Diameter

#### 3.3.2.1  Innerduct shall be equivalent to Duraline specification PE3408 for ribbed innerduct.

#### 3.3.2.2  Construction shall be of high density polyethylene

#### 3.3.2.3  Innerduct shall be supplied by the manufacturer with a measured pull line in increments not greater than one meter.

#### 3.3.2.4  Maximum pull strength of innerduct shall be a minimum of twelve hundred (1200) pounds.

#### 3.3.2.5  Tensil strength at breaking shall be not less than 4000 psi (ASTM

#### D-638 test method).

#### 3.3.2.6   In-duct pull line shall have a breaking strength of not less than twelve hundred (1200) pounds.

#### 3.3.2.7  Minimum bend radius shall be ten inches (10").

#### 3.3.2.8  Inside diameter shall be 1.00" +/- 0.015".

#### 3.3.2.8  Outside diameter shall be 1.320" +/- 0.020".

## 4.0 	VENDOR SUBMITTALS:

## 4.1  Vendor Information

## Vendor shall provide the following information as their response to this RFQ.

### 4.1.1  Vendor Name: ______________________________

### 4.1.2  Vendor representative preparing this RFQ:________________________

### 4.1.3  Vendor Mailing Address: ___________________________________

____________________________________

____________________________________

### 4.1.4  Vendor Representative Phone Number:   ________________________

### 4.1.5  Vendor shall use the pricing submittal sheet ONLY for their responses.

### 4.1.6  All pricing shall include applicable sales tax.

### 4.1.7  Vendor shall state shipping and handling cost separately.

### 4.1.8  Vendor shall state costs, if any, for cutting cable and innerduct to specific lengths on individual reels.

## 4.2  Pricing

### 4.2.1.  Vendor shall submit a price for thirty-four thousand, seven hundred and fifty feet (34,750') of forty-eight (48) strand multi-mode fiber optic cable as defined by specifications in Section 3.1 (above).

#### Total multi-mode fiber optic cable  $ ______________________________

#### Shipping and handling costs for above $ ________________

#### Cost for cutting cable to specific lengths on reel(s)  $ _________________

### 4.2.2.  Vendor shall submit unit per foot price for the forty-eight (48) strand multi-mode fiber optic cable as defined by specifications in Section 3.1 (above).

#### Per foot multi-mode fiber optic cable  $_______________________/foot

### 4.2.3  Vendor shall submit a price for thirty-four thousand, seven hundred and fifty feet (34,750') of forty-eight (48) strand multi-mode and twelve (12) strand single mode composite fiber optic cable as defined by specifications in Section 3.2 (above).

### (Bid Alternative One).

#### Total composite fiber optic cable  $______________________________

#### Shipping and handling costs for above: $________________

#### Cost for cutting cable to specific lengths on reel(s)  $ ______________

### 4.2.4  Vendor shall submit a unit per foot price for forty-eight (48)strand multi-mode and twelve (12) strand single mode composite fiber optic cable as defined by specifications in Section 3.2 (above)

### (Bid Alternative One).

#### Per foot composite fiber optic cable  $_____________________/foot

### 4.2.5   Vendor shall submit a price for thirty-seven thousand, three hundred feet (37,300') of one and one-quarter inch (1.25") diameter fiber optic innerduct as defined by specifications in Section 3.3 (above). Of this amount, eighteen thousand, six hundred and fifty feet (18,650') will be orange or orange-striped, and eighteen thousand, six hundred and fifty feet (18,650') will be black or black-striped.

#### Total one and one-quarter inch fiber optic innerduct    $__________________

#### Shipping and handling costs for above: $________________

#### Cost for cutting innerduct to specific lengths on reel(s)  $ ______________

### 4.2.6  Vendor shall submit a unit per foot price for one and one-quarter inch (1.25") diameter fiber innerduct as defined by specifications in Section 3.3 (above).

#### Per foot one and one-quarter inch innerduct   $______________________/foot

### 4.2.7 Vendor shall submit a price for twenty-two thousand, nine hundred feet (22,900') of one inch (1.00") diameter fiber optic innerduct as defined by specifications in Section 3.3 (above). Of this amount, eleven thousand, four hundred and fifty feet (11,450')  will be orange or orange-striped, and eleven thousand, four hundred and fifty feet (11,450') feet will be black or black-striped.

#### Total one inch innerduct   $ ______________________________

#### Shipping and handling costs for above: $________________

#### Cost for cutting innerduct to specific lengths on reel(s)  $ ______________

### 4.2.8 Vendor shall submit a unit per foot price for one inch (1.00") diameter fiber optic innerduct as defined by specifications in Section 3.3 (above).

#### Per foot one inch innerduct   $_____________________________

## 4.3  Specifications

### Ordering Part Numbers and Samples

### Vendor shall submit the specific manufacturer part number and Vendor ordering number for each component defined in Section 3 and priced in Section 4.1.

### 4.3.1  Forty-eight (48) strand multi-mode fiber optic cable as defined by specifications in Section 3.1 and priced in 4.1.1 and 4.1.2 (above)

#### Ordering Part # ______________________

#### Manufacturer Part # _________________________

### 4.3.2  Forty-eight (48) strand multi-mode and twelve (12) strand single mode composite fiber optic cable as defined by specifications in Section 3.2  and priced in 4.1.3 and 4.1.4 (above)

### (Bid Alternative One).

#### Ordering Part # ______________________

#### Manufacturer Part # _________________________

### 4.3.3  One and one-quarter inch (1.25") diameter fiber optic innerduct as defined by specifications in Section 3.3 and 4.1.5 and 4.16 (above).

#### Ordering Part # ______________________

#### Manufacturer Part # _________________________

### 4.3.4  One inch (1.00") diameter fiber optic innerduct as defined by specifications in Section 3.3 and 4.1.7 and 4.1.8 (above).

#### Ordering Part # ______________________

#### Manufacturer Part # _________________________

## 4.4   Manufacturer Specification Sheets

## Vendor shall submit manufacturer specification sheets for each of the items identified in 4.3.1 (above).

## 4.5  Samples

### Vendor shall submit, with their response to the RFQ,  a three foot (3') sample of each fiber optic cable(s) and innerduct(s) proposed in their written response.

### Each sample must be clearly marked with the name of the vendor submitting the sample and the Ordering and Manufacturer Number (s) for the cable sample.

## 4.6  Delivery

### Vendor shall acknowledge the requested delivery schedules for fiber optic innerduct and fiber optic cable as defined in Section 1.16 of this RFQ.

### 4.6.1  I acknowledge that delivery of forty-eight (48) strand multi-mode fiber optic cable to the campus can be made by 4:00pm, August 25, 1995.

### _________________________________________________

### Signature                                                                Date

### 4.6.2  I acknowledge that delivery of composite forty-eight (48) multi-mode and twelve (12) single mode fiber optic cable to the campus can be made by 4:00pm, August 25, 1995.

### (Bid Alternative One).

### _________________________________________________

### Signature                                                               Date

### 4.6.3   I acknowledge that delivery of one and one quarter inch (1.25") fiber innerduct to the campus can be made by 4:00pm, July 28, 1995.

### _________________________________________________

### Signature                                                              Date

### 4.6.4  I acknowledge that delivery of one inch (1.00") fiber innerduct to the campus can be made by 4:00pm,  July 28, 1995.

### _________________________________________________

### Signature                                                             Date

## 4.7  Warranty

### 4.7.1  Specify the manufacturer's warranty for each component to be acquired as part of this RFQ.  Attach a copy of manufacturer warranty to your response.

### 4.7.2  Specify your (Vendor) warranty for each component to be acquired under this RFQ.  This warranty must be in effect for at least one (1) year from the date of the University's acceptance of the all materials. Attach a copy of Vendor  warranty to your response.

### 4.7.3. Maximum time frame for replacement of warranted material after notification to the Vendor of University rejection of material.

### 4.7.4  Identify name, title and phone number of Vendor agent who will be responsible for fulfilling warranty provisions.

### Vendor Warranty Agent Name  __________________________________

### Vendor Warranty Agent Title ___________________________________

### Vendor Warranty Agent Address ________________________________

### ________________________________

________________________________

### Vendor Warranty Agent Phone Number  ___________________________

## * * * * * *